## Slide 1: Thailand Water Supply System Project
By:
Stephen Bonk
Joseph Moore
Kevin Dischino

## Slide 2: Preliminary Site Assessment
Village of Hantham: subset of Longkhot, Thailand
Inadequate water supply during the dry season
159 Households and 453 People
Average Water Usage: 200 L/day per Household
Gathered Survey Data
Collected Soil Sample
Determined available resources

## Slide 3: Survey Data

## Slide 4: Design Goals
Supply entire village
Sustainably powered pumping system
Easily maintained and constructible Storage System
Distribution System
O & M Manual
Extremely Economical

## Slide 5: Water Usage
Average Annual Flow is 200 L/day per Household
0.013 cfs for the total village
Total Storage Volume for 3 day supply = 3,369 cf
Maximum Hourly Flow per Year is 270% of Average Flow per Year
Maximum Hourly Flow per Year = 0.0351 cfs

## Slide 6: Storage Tank Elevation

## Slide 7: Storage Tank Elevation

## Slide 8: Storage Tank Elevation
3 in Diameter for Pipe A
  Site 1 and Site 2 Inadequate
  Site 3 Adequate, No Tower Necessary
Place Storage Tanks at Site 3, Ground Level
  Orange House Water Pressure will be 4 psi under Dynamic Conditions during Max Hour Flow

## Slide 9: Pumping System
Submersible Pump
Pusher Pump
System Energy
Future Design Considerations
  Manufacturer Specifications for Pumps
  Solar Panel System Power Requirements

## Slide 10: Water Distribution System Design

## Slide 12: Process
Split Section A into Pipe Branches
Maximum Hourly Flow per Year:
    2.207x10^-4 cfs for each household
Determine flow through each Pipe
Darcy – Weisbach Equation

## Slide 13: Section A Schematic

## Slide 14: Design of Pipe 1
Assume Maximum Velocity between 10-20ft/s
Find Minimum Diameter needed (A = Q/V)
  For Pipe 1 of 13Q:
    Diam = 0.16” – 0.23”
For 0.25” Diameter
  Head Loss = 658 feet (Too Large)
For 1” Diameter – Head Loss = 0.98 feet
For 2” Diameter – Head Loss = 0.0242 feet

## Slide 15: Total Headloss
1” Diameter – 3.025 feet
2” Diameter – 0.079 feet
In the Future…
  Will be Utilizing WaterCAD to analyze entire village

## Slide 16: Foundation
Soil Profile
  γ=105 pcf φ = 30o c = 0 psf (Normally Consolidated Soil)
Soil Classification
  USCS: Silty or Clayey Sand
Minimum soil characteristics
  γ= 80 pcf φ= 28o c = 0 psf
Bearing capacity: Min=4000 psf, Estimated=13000 psf
Factor of Safety: Estimated=16.1, Min=4.75

## Slide 17: Water Tank Design
Type
  Reinforced Concrete Rectangular Tank (25’x25’x6’)
  Fiberglass or Reinforced Concrete Circular Tank ( Dia.=18’)
  12” thickness of wall and 8” slab.
Availability
  Reinforced Concrete only available, no fiberglass
Cover: Reinforced Concrete or Sheet Metal
Placement: Site 3
Construction Time

## Slide 18: Budget
Material Cost
  Pumping System $6,500
  Reinforced Concrete Tank $8,000
Travel Cost
  $2,500 per person

## Slide 19: Gantt Chart

## Slide 20
Questions or Concerns?