## Slide 1: Thailand Water Supply System Project
By:
Stephen Bonk (Team Leader)
Kevin Dischino
Joseph Moore

## Slide 2: Preliminary Site Assessment
Village of Hantham: subset of Longkhot, Thailand
Inadequate water supply during the dry season
159 Households and 453 People
Average Water Usage: 200 L/day per Household
Gathered Survey Data
Collected Soil Sample
Determined available resources

## Slide 3: Survey Data

## Slide 4: Design Goals
Supply entire village
Sustainably powered pumping system
Easily maintained and constructible Storage System
Distribution System
O & M Manual
Extremely Economical

## Slide 5: Water Resources and Hydraulics Design

## Slide 6: Water Usage
Average Annual Water Usage is 200 L/day per Household
Total Village Usage is 1,123 cf/day
Total Tank Volume for 3 day supply = 3,369 cf
Maximum Hourly Flow per Year is 270% of Average Flow per Year
Maximum Hourly Flow per Year = 0.0351 cfs

## Slide 7: Minimum Storage Tank Elevation
Must provide adequate water pressure for highest household in the village
Is structure required to provide additional elevation?

## Slide 8: Minimum Storage Tank Elevation

## Slide 9: Minimum Storage Tank Elevation

## Slide 10: Minimum Storage Tank Elevation
Major Head Loss in Pipe A:
  1 in Diameter  Major Head Loss = 323.5 ft
  2 in Diameter  Major Head Loss = 11.7 ft
  3 in Diameter  Major Head Loss = 1.7 ft
Minimum Diameter of Pipe A for Maximum Velocity of 10 fps = 0.8 in
3 in Diameter Pipe Selected

## Slide 11: Minimum Storage Tank Elevation
Using 3 in Diameter Pipe A
  Site 1 and Site 2 Inadequate
  Site 3 Adequate, No Tower Necessary
Place Storage Tanks at Site 3, Ground Level
  Orange House Water Pressure will be 4 psi under Dynamic Conditions during Max Hour Flow

## Slide 12: Pumping System
Submersible Pump
Pusher Pump
System Energy

## Slide 13: Pumping System
Chart: 1 in Pipe System Head Curve
| 0 | 2.2441499999999999 | 4.4883000000000024 | 5.8347899999999964 | 6.7324499999999992 | 8.9766000000000048 | 11.220750000000001 | 13.464900000000002 | 15.709050000000001 | 17.953199999999981 | 20.197350000000014 | 22.44149999999998
1 inch Pipe | 424.4 | 428.8903 | 438.9501 | 448.1661 | 454.9447 | 474.8031 | 500.1091 | 529.0351 | 560.8502 | 598.7221 | 640.0922 | 684.5951

## Slide 14: Pump System
Future Design Considerations
  Manufacturer Specifications for Pumps
  Solar Panel System Power Requirements
  Tank Level Switch

## Slide 15: Water Distribution System Design

## Slide 16: Site View

## Slide 17: Process
Split Section A into Pipe Branches
Maximum Hourly Flow per Year:
    2.207x10^-4 cfs for each household
Determine flow through each Pipe
Darcy – Weisbach Equation
    Reynold’s Number, ε/D
Use of WaterCAD

## Slide 18: Section A Schematic
Pipe 3
200 ft.
Pipe 2
320 ft.
Pipe 1 445 ft.
Pipe 4 = 200 ft.
Pipe 5
350 ft.
Pipe 6
250 ft.
Pipe 7 = 275 ft.

## Slide 19: Design of Pipe 1
Assume Maximum Velocity between 10-20ft/s
Find Minimum Diameter needed (A = Q/V)
  For Pipe 1 of 13Q:
    Diameter = 0.16” – 0.23”
For 0.25” Diameter
    Head Loss = 658 feet (Too Large)
For 1” Diameter – Head Loss = 0.98 feet
For 2” Diameter – Head Loss = 0.0242 feet

## Slide 20: WaterCAD Schematic

## Slide 21: Input / Output

## Slide 22: Total Head Loss
Hand Calculations
    1” Diameter – 3.025 feet
    2” Diameter – 0.079 feet
WaterCAD Results
    2” Diameter – 0.0665 ft.

## Slide 23: WaterCAD Output
Pipe | Start Node | Stop Node | Diameter (in) | Material | Flow (cfs) | Headloss Gradient (ft/ft) | Length (ft) | Headloss (ft)
P-1 | T-1 | J-1 | 3 | PVC | 0.035091 | 0.000867 | 1,903 | 1.649901
P-2 | J-1 | J-2 | 4 | PVC | 0.006621 | 0.000008 | 853 | 0.006824
P-5 | J-4 | J-5 | 2 | PVC | 0.000221 | 0.000004 | 200 | 0.0008
P-6 | J-2 | J-6 | 2 | PVC | 0.003752 | 0.000083 | 200 | 0.0166
P-13 | J-2 | J-10 | 2 | PVC | 0.002869 | 0.000052 | 150 | 0.0078
P-15 | J-10 | J-11 | 0.75 | PVC | 0.000221 | 0.000198 | 25 | 0.00495
P-18 | J-12 | J-13 | 0.75 | PVC | 0.000221 | 0.000198 | 100 | 0.0198
P-19 | J-10 | J-17 | 2 | PVC | 0.002428 | 0.000046 | 30 | 0.00138
P-20 | J-17 | J-12 | 2 | PVC | 0.001986 | 0.000036 | 85 | 0.00306
P-21 | J-17 | J-18 | 0.75 | PVC | 0.000221 | 0.000198 | 80 | 0.01584
P-23 | J-19 | J-3 | 2 | PVC | 0.001104 | 0.00002 | 25 | 0.0005
P-24 | J-19 | J-20 | 0.75 | PVC | 0.000221 | 0.000202 | 25 | 0.00505
P-25 | J-12 | J-21 | 2 | PVC | 0.001545 | 0.000028 | 115 | 0.00322
P-26 | J-21 | J-19 | 2 | PVC | 0.001324 | 0.000024 | 40 | 0.00096

## Slide 24: Geotechnical and Storage Tank Design

## Slide 25: Foundation
Soil Profile
  γ=105 pcf φ = 30o c = 0 psf (Normally Consolidated Soil)
Soil Classification
  USCS: Silty or Clayey Sand
Minimum soil characteristics
  γ= 80 pcf φ= 28o c = 0 psf
Bearing capacity: Min=3855.9 psf, Estimated=13062.84 psf
Factor of Safety: Estimated=16.09, Min=4.75

## Slide 26: Soil Properties
Chart: Sieve Analysis
| 0.59899999999999998 | 0.4220000000000001 | 0.251 | 0.10400000000000001 | 7.5000000000000011E-2
 | 0.99336 | 0.81503 | 0.63941 | 0.35456 | 0.16747

## Slide 27: Foundation Spreadsheet

## Slide 28: Water Tank Design
Type
  Reinforced Concrete Rectangular Tank (25’x25’x6’)
  Fiberglass or Reinforced Concrete Circular Tank ( Dia.=18’)
  12” thickness of wall and 8” slab.
  Formwork
Availability
  Reinforced Concrete only available, no fiberglass
Cover: Reinforced Concrete or Sheet Metal
Placement: Site 3
Construction Time

## Slide 29: Rectangular Cantilever Concrete Tank
Height: 6 feet
Depth of Embedment: 2 feet
Top of Wall: 8” Concrete
Heel and Toe slab use same reinforcement
Water Stirrup (Rubber)

## Slide 30: Rectangular Cantilever Storage Tank

## Slide 31: Gantt Chart

## Slide 32: Budget

## Slide 33
Questions?